## Events & Error code description
Code | Original description | Short description | LED behaviour | Comments | Battery Error Status Register PDO 0x481
0x01 | ERROR_NR_OVER_TEMP_LADEN_ZELLEN | Cell over temperature during charging | Solid red | The cell temperature in a module exceeds specified range. Charging on all modules are stopped. Charging is automatically resumed when the temperature of all cells in all modules are within range | Bit 12
0x02 | ERROR_NR_UNDER_TEMP_LADEN_ZELLEN | Cell under temperature during charging | Solid red | The cell temperature in a module is below temperature range. Charging on all modules are stopped. Charging is automatically resumed when the temperature of all cells in all modules are within range | Bit 12
0x03 | ERROR_NR_OVER_TEMP_LADEN_FET | Charge FET's above temperature limit during charging | Solid red | The Charge FET's temperature in a module exceeds specified range. Charging on all modules are stopped. Charging is automatically resumed when the temperature of all FET's in all modules are within range | Bit 12
0x04 | ERROR_NR_OVER_TEMP_ENTLADEN_ZELLEN | Cell over temperature during Discharging | Solid red | The cell temperature exceeds temperature range. Discharging on all modules are stopped. Discharging can only be resumed by charging or Off/On activation if the temperature of all cells in all modules are within range | Bit 13
0x05 | ERROR_NR_UNDER_TEMP_ENTLADEN_ZELLEN | Cell under temperature during Discharging | Solid red | The cell temperature below temperature range. Discharging on all modules are stopped. Discharging can only be resumed by charging or Off/On activation if the temperature of all cells in all modules are within range | Bit 13
0x06 | ERROR_NR_OVER_TEMP_ENTLADEN_FET | Discharge FET's above temperature limit during discharging | Solid red | The Discharge FET's temperature in a module exceeds specified range. Discharging on all modules are stopped. Discharging can only be resumed by charging or Off/On activation if the temperature of all FET's in all modules are within range | Bit 13
0x07 | ERROR_NR_OVER_TEMP_CLAMP | Not used
0x08 | ERROR_NR_OVER_VOLTAGE | Cell over voltage during charge | Solid red | A cell over voltage during charge in any module terminates charge of all modules. Over voltage during charge can only happen if the charger is defect or a non-authorized charger is used. The modules are automatically reset by a discharge detection | Bit 11
0x09 | ERROR_NR_UNDER_VOLTAGE | Cell under voltage during discharge | Solid red | When a cell block in a module is depleted below value in Object 0x2104.b or Object 0x2104.c, the complete module is disconnected from the pack. The remaining modules in a pack will continue to operate. The condition is reset by charging to an SoC level of what is defined in 0x2804.3 (Typically: 2%) | Bit 10
0x0a | ERROR_NR_DEEP_LOW_VOLTAGE | Cell voltage too low | Flashing red | If a cell block in a module is deep discharged, this module is permanently disconnected from the pack. The remaining modules in a pack are working normally. The module must be replaced. | Bit 14
0x0b | ERROR_NR_CELL_DISBALANCE | Severe Cell unbalance within a module | Flashing red | If the cell block imbalance inside a module exceeds 200mV, the module will open both FETs and disconnect charging and discharging. If the imbalance drops below 100mV, the failure is reset.
0x0c | ERROR_NR_AKKU_PACK_SPN_MIN_ERROR | Not used
0x0d | ERROR_NR_AKKU_PACK_SPN_MAX_ALARM | Overvoltage Pack | Solid red | If the module voltage exceeds 4.5V x number of serial cells, charging is stopped. Charging is resumed if the module voltage drops by 1V. Only the specific module will open the Charge FET. | Bit 5
0x0e | ERROR_NR_AKKU_PACK_FUSED_SPN_DIFF_ERROR | Not used
0x0f | ERROR_NR_AKKU_PWR_SPN_DIFF_ERROR | Voltage difference between sum of single cells and module voltage | Solid red | The difference of the sum of single cell voltages and the module voltage is too high. Allowed difference is 1V x number of serial cells. | Bit 14
0x10 | ERROR_NR_AKKU_PWR_SPN_MIN_ERROR | Measured module voltage too low. | Solid red | The module voltage is less than 2V x number of serial cells. Reset condition: Voltage 1V greater than 2V x number of serial cells. | Bit 14
0x11 | ERROR_NR_AKKU_PWR_SPN_MAX_ERROR | Not used
0x12 | ERROR_NR_AKKU_NETZ_SPN_MIN_ERROR | Not used
0x13 | ERROR_NR_AKKU_NETZ_SPN_MAX_ALARM | Not used
0x14 | ERROR_NR_AKKU_REKUPERATIOM_SPN_MAX_ALARM | Not used
0x15 | ERROR_NR_I_CHARGE_SC | Short-circuit current during charging | Solid red | The charge current exceeds 300 Ampere for more than 300 µS. This can only happen if the charger is defect. Charging on all modules is stopped. The module is reset by an Off/On activation or by connecting a load | Bit 3
0x16 | ERROR_NR_I_CHARGE_OCC_1 | Over current during charging | Solid red | The charge current exceeds 65 Ampere for more than 3 seconds. This can only happen if the charger is defect. Charging on all modules is stopped. The module is reset by an Off/On activation or by connecting a load | Bit 8
0x17 | ERROR_NR_I_CHARGE_OCC_2 | Over current during charging | Solid red | The charge current exceeds 85 Ampere for more than 50 mS. This can only happen if the charger is defect. Charging on all modules is stopped. The module is reset by an Off/On activation or by connecting a load | Bit 8
0x18 | ERROR_NR_I_CHARGE_OCC_3 | Not used
0x19 | ERROR_NR_I_DISCHARGE_SC | Short-circuit current during discharging | Solid red | The discharge current exceeds 300 Ampere for more than 300 µS. This can happen if the power terminals are shorted, if the capacitance of the load is too big (Inrush) or if a single module is driving an excessive load. The module is reset by an Off/On activation or by connecting a charger. | Bit 4
0x1a | ERROR_NR_I_DISCHARGE_OCD_1 | Over current during discharging | Solid red | The discharge current exceeds 65 Ampere for more than 3 seconds. This happens if the power for a single module is too high and it happens if e.g. 8 of 10 modules in a huge machine is depleted. The remaining 2 modules cannot support the load of the machine. The module is reset by an Off/On activation or by connecting a charger. | Bit 9
0x1b | ERROR_NR_I_DISCHARGE_OCD_2 | Over current during discharging | Solid red | The discharge current exceeds 85 Ampere for more than 50 mS. This happens if the power for a single module is too high and it happens if e.g. 9 of 10 modules in a huge machine is depleted. The remaining module cannot support the load of the machine. The module is reset by an Off/On activation or by connecting a charger. | Bit 9
0x1c | ERROR_NR_I_DISCHARGE_OCD_3 | Not defined in ComBat-II | N/A | N/A
0x1d | ERROR_NR_I_AKKU_DIFF_ERROR | Difference of current measurement | Flashing red | The filtered and unfiltered current measurement differs by 10%. Can only happen if there is a HW damage in the current measurement circuity.
0x1e | ERROR_NR_SCND_SPN_MIN_ERROR | Not used
0x1f | ERROR_NR_SCND_SPN_MAX_ERROR | Not used
0x20 | ERROR_NR_SCND_UC_FET_ENABLE | Not used
0x21 | ERROR_NR_SCND_CURRENT_SENSE_EIN | Not used
0x22 | ERROR_NR_SCND_VOLTAGE_SENSE_EIN | Not used
0x23 | ERROR_NR_SCND_TEMP_CELL_SENSE_EIN | Not used
0x24 | ERROR_NR_SCND_TEMP_FET_SENSE_EIN | Not used
0x25 | ERROR_NR_SCND_PYRO_FUSE_EJECT_SENSE_EIN | Not used
0x26 | ERROR_NR_SCND_I_DISCHARGE_FET_ERROR | Not used
0x27 | ERROR_NR_SCND_I_CHARGE_FET_ERROR | Not used
0x28 | ERROR_NR_SCND_VOLTAGE_ERROR | Not used
0x29 | ERROR_NR_ADC_SPN_MIN_SCALE | A value close to the limit of the ADC is measured. | Flashing red | A voltage value greater than 5V is measured which can only happen if there is a damage of the measuring circuity. | Bit 10
0x2a | ERROR_NR_ADC_SPN_MAX_SCALE | A value close to the limit of the ADC is measured. | Flashing red | A voltage value less than -5V is measured which can only happen if there is a damage of the measuring circuity. | Bit 11
0x2b | ERROR_NR_ADC_TEMP_ZELLEN_MIN_SCALE | Cell temperature sensor value too high | Flashing red | A cell temperature sensor reports a temperature above +125 °C, which typically means that a temperature sensor is shorted. The module is permanently disconnected from the pack. The remaining modules in a pack are working normally. The module must be replaced. | Bit 14
0x2c | ERROR_NR_ADC_TEMP_ZELLEN_MAX_SCALE | Cell temperature sensor value too low | Flashing red | A cell temperature sensor reports a temperature below -40 °C, which typically means that a temperature sensor is disconnected. The module is permanently disconnected from the pack. The remaining modules in a pack are working normally. The module must be replaced.
0x2d | ERROR_NR_ADC_TEMP_FET_MIN_SCALE | FET temperature sensor value too high | Flashing red | A FET temperature sensor reports a temperature above +125 °C, which typically means that a temperature sensor is shorted. The module is permanently disconnected from the pack. The remaining modules in a pack are working normally. The module must be replaced. | Bit 14
0x2e | ERROR_NR_ADC_TEMP_FET_MAX_SCALE | FET temperature sensor value too low | Flashing red | A FET temperature sensor reports a temperature below -40 °C, which typically means that a temperature sensor is disconnected. The module is permanently disconnected from the pack. The remaining modules in a pack are working normally. The module must be replaced.
0x2f | ERROR_NR_ADC_TEMP_CLAMP_MIN_SCALE | Not used
0x30 | ERROR_NR_ADC_TEMP_CLAMP_MAX_SCALE | Not used
0x31 | ERROR_NR_ADC_I_CHARGE_MIN_SCALE | Not used
0x32 | ERROR_NR_ADC_I_CHARGE_MAX_SCALE | A value close to the limit of the ADC is measured. | Flashing red | A current value greater than +400 A is measured. NOTE: The delay is longer than the short circuit protection. | Bit 8
0x33 | ERROR_NR_ADC_I_DISCHARGE_MIN_SCALE | Not used
0x34 | ERROR_NR_ADC_I_DISCHARGE_MAX_SCALE | A value close to the limit of the ADC is measured. | Flashing red | A current value less than -600A is measured. NOTE: The delay is longer than the short circuit protection. | Bit 9
0x35 | ERROR_NR_I_DISCHARGE_FET_ERROR | Discharge FET is shorted | Flashing red | Discharging cannot be stopped but recharge is not possible. The module must be replaced | Bit 6
0x36 | ERROR_NR_I_CHARGE_FET_ERROR | Charge FET is shorted | Flashing red | Discharging and Charging is not possible. The module must be replaced | Bit 7
0x37 | ERROR_NR_I_DISCHARGE_CHARGE_FET_ERROR | Not used
0x38 | ERROR_NR_TEMP_DISCHARGE_ERROR_LOCK | Discharge Error Lock | Solid red | This flag is set in combination with Error 0x04 / 0x05 / 0x06. | Bit 15
0x39 | ERROR_NR_TEMP_CHARGE_ERROR_LOCK | Charge Error Lock | Solid red | This flag is set in combination with Error 0x01 / 0x02 / 0x03.
0x3a | ERROR_NR_OVER_CHARGE_CURRENT_ALARM_RECUPERATION | Overcharge current due to recuperation | Solid red | Pack over current during discharge can only happen due to recuperation. The modules are automatically reset by a discharge detection | Bit 2
0x3b | ERROR_NR_OVER_CHARGE_CELL_VOLTAGE_ALARM_RECUPERATION | Overcharge cell voltage due to recuperation | Solid red | Cell over voltage during discharge can only happen due to recuperation. The modules are automatically reset by a discharge detection | Bit 2
0x3c | ERROR_NR_24V_SPN_MIN_ERROR | 24-volt supply below limit | Flashing red | 24V supply of the BMS is lower than 16V. | Bit 15
0x3d | ERROR_NR_24V_SPN_MAX_ERROR | 24-volt supply above limit | Flashing red | 24V supply of the BMS is higher than 26V. | Bit 15
0x3e | ERROR_NR_CAN_NETWORK_NOT_CONF_NODE_ID | Node-ID are not assigned | Flashing Orange | The module cannot communicate on CAN and charging is not possible
0x3f | ERROR_NR_CAN_NETWORK_DOUBLE_NODE_ID | NodeID conflict | Flashing Orange | The module cannot communicate with other Nodes on CAN and charging is not possible
0x40 | ERROR_NR_PARAMETER_CONFIGURATION_ERROR | Parameter outside range | Flashing red | The version of the module is identified from the SW via an external ID resistors. If the ID resistor coding doesn´t fit to the programming of the specific variant (24V / 36V / 48V), this failure is set. | Bit 15
Pushed (Always available)
Pulled (Available upon request)